Stormwater: Engineering Drawing Checklist

Privacy Statement: The information collected on this form will be used by Brisbane City Council – Development Assessment for the purpose of ensuring all key design criteria is provided as part of Operational Works & Compliance Assessment application submissions.

It is the responsibility of the consultant to ensure all information is provided in accordance with Brisbane City Council’s Codes and Policies to accommodate a streamlined approval process.

| Site Address: |  |
| --- | --- |
| High Level Application #: |  |
| Condition Reference #: |  |

| Description | Completed |  | Comments To be completed for all non-standard designs |
| --- | --- | --- | --- |
|  | YES | NO |  |
| Preliminary Requirements Refer to Section 1.5 > Chapter 1 Introduction > Infrastructure Design (ID) PSP > Schedule 6 PSP Note: Drafting must be of a standard that is acceptable for construction in civil engineering & architectural practice, in accordance with the requirements of AS 1100.101-1992 Technical drawing – General principles. |  |  |  |
| Have plans been signed & checked by RPEQ together with RPEQ number and date shown on title block? |  |  |  |
| Plans assessed against all town planning conditional requirements & approved plans: - ROL/MCU conditions - Any road dedications / corner truncations |  |  |  |
| Leading Drawing must contain: - Council reference number; - Site Address (consistent with application); - Locality plan (showing stage boundaries if applicable); - Drawing index; - List of all Council standard drawings used; - List of all consultant standard drawings used (copies to be attached); - Full Legend; - Existing & Proposed Contours |  |  |  |
| Scales: Recommended Scales are 1:1, 1:2, 1:5 (multiplied by integral powers of 10) - Plans – 1:1000 or 1:500 (roof-water reticulation layout plans should be drawn in the 1:500 scale); - longitudinal sections – (i) horizontal 1:1000 and vertical 1:100; or (ii) horizontal 1:500 and vertical 1:50. - Intersection details – 1:200, 1:100 or 1:250; - cross-sections – 1:100; - Engineering details – 1:20 or 1:10. - A north point and legend is to be shown on all drawings. |  |  |  |
| Dimensions: - All dimensions in metric units. - Linear dimensions in metres. - Excl. detailed drawings (maintenance holes/ kerb & channel) – millimetres. - Reduced levels of roadworks & stormwater drainage expressed & rounded to 3 decimal places (0.001m) - Chainages to 3 decimal places (0.001m) - Road cross-sections provided at 20m intervals (further subdivision of 10m to 5m where necessary at horizontal or vertical clearances). - Road & Pipe grades must be show to 3 significant figures (e.g. 2.635%). |  |  |  |

| General Checks |  |  |  |
| --- | --- | --- | --- |
| Ecology Triggers |  |  |  |
| - Are there any Ecology conditions (e.g. vegetation management plan, landscape, ecology or NALL) which may affect the proposed designs. - If YES: is the required VMP OpWorks approved? - If NO: can the application be approved with the generic stamp and amendments in red (will required advice from BCC Ecologist). |  |  |  |
| - Is the site on the contaminated land register or Environmental Land Register? |  |  |  |
| - Identify areas subject to Vegetation protection or NALL on plans. |  |  |  |
| Flooding & Waterway implications |  |  |  |
| - Is the site affected by flooding? - If YES; details of minimum habitable floor levels are to be clearly identified on the layout plans where allotments are to be filled to provide flood immunity (refer to Flood Overlay Code & Planning Approval conditions). |  |  |  |
| - Effect on neighbouring properties examined (ponding) |  |  |  |
| - Location of Waterway Corridors identified on plans (if applicable). |  |  |  |
| - Location of all flooding extents including drainage/overland flow easements identified. |  |  |  |
| Approved SBSMP |  |  |  |
| - Was there an approved SBSMP as part of the High Level Development Application? - Are designs consistent with approved SBSMP (LPD etc.) |  |  |  |
| SW Quality |  |  |  |
| - Are there any SW Quality devices (basins) proposed as part of the design? - Were they approved under a separate application? [Provide Details – application approval number] |  |  |  |
| Stormwater Layout Plan |  |  |  |
| Existing Site Characteristics |  |  |  |
| - Surface Levels - Accesses - Services - Larger Trees - Guard Rails - Retaining Walls - Combined Services - Road reserve boundaries & road identification - Contours (existing AND proposed) |  |  |  |
| Proposed Characteristics |  |  |  |
| - Location of stormwater & roofwater lines (including size), manholes, gullies, outlets, inlets, roofwater inspection pits, etc. - Swales, bunds,etc. provided as required - Field Inlets provided for overland flow |  |  |  |
| Longitudinal Sections |  |  |  |
| Details |  |  |  |
| - Chainages, existing & design levels, inverts, pipe class, grades & diameters |  |  |  |
| - Gully numbers, type of gully & size of lintel |  |  |  |
| - Manhole depths & diameters - Max 90m between manholes. |  |  |  |
| - Service crossings (if applicable) |  |  |  |
| - Pipe class, grades, capacity & diameters |  |  |  |
| - Invert levels of inlets/outlets (incl. free outlets & creek bed). |  |  |  |
| Hydraulics |  |  |  |
| - Long sections show design storm event & HGL’s - HGL is greater than 150mm from surface level of manholes or kerb inlets. - Starting HGL for pipe discharging to waterway or channel is greater of known flood level or obvert of pipe. |  |  |  |
| - Minor system design for road is: - 2yr ARI for minor roads - 10yr ARI for major roads |  |  |  |
| - Pipe Velocities are: - No greater than 4.7m/s - Not less than 0.6 m/s |  |  |  |
| - Downstream pipes are not smaller than upstream pipes. |  |  |  |
| - Pipe outlet velocity into natural creek/channel is <2m/s & riprap provided (d50 of 300mm min) that is 3 times length of outlet pipe diameter. |  |  |  |
| Roofwater Drainage |  |  |  |
| Lawful Point of Discharge |  |  |  |
| - Provided in accordance with High Level approval conditions & in accordance with Infrastructure Design PSP and relevant Brisbane Standard Drawings. |  |  |  |
| Roofwater Pipes |  |  |  |
| - 1-2 lots is a 150mm diameter UPVC @ >1% grade - 3-4 lots is a 225mm diameter UPVC @ >0.5% grade - 5-6 lots is a min 300mm diameter UPVC at >0.5% grade. |  |  |  |
| - Connection for each property tied to property boundary. |  |  |  |
| - Provided with Roofwater Inspection Manholes where required and in maximum 100m intervals. |  |  |  |
| - Drainage to allotments on high side of one-way crossfall streets to be taken to gullies. |  |  |  |
| - Discharge to kerb & channel limited to 30L/s @ Q20. - RHS or stormwater pipes in Road verges not protruding onto adjacent property front verge. - RHS location minimum 300mm clearance from driveway tapers. |  |  |  |
| Easements |  |  |  |
| - Shown for 225mm dia pipe & greater or over any upstream connection (Refer to IDPSP for details.) |  |  |  |
| Upstream Connection |  |  |  |
| - Extended to upstream lot (stub capped @ boundary) |  |  |  |
| - Designed for ultimate catchment (assume fully developed given zoning). |  |  |  |
| - Drains to LPD with sufficient capacity - Gully Pit (ACCEPTABLE) - Kerb & Channel (UNACCEPTABLE) |  |  |  |
| Manholes & Chambers |  |  |  |
| Key Details |  |  |  |
| - Manhole/chamber size indicated - Identification numbers - Location change shown - Connecting pipes shown |  |  |  |
| - Minimum distance between outside walls of pipes is greater than 150mm in manholes |  |  |  |
| - Step irons provided where manhole depth >1.35m - Fixed ladder provided where manhole depth > 3m (UNDESIRABLE) - Look at alternatives to reduce depth - Larger pipes = less maintenance. |  |  |  |
| Inlets / Outlets |  |  |  |
| Key Details |  |  |  |
| - Invert levels (in accordance with QUDM Section 7.5 for inlets & Section 8 for outlets) |  |  |  |
| - Grades - Avoid long sections of very flat pipelines - Min.velocity of 1m/s for self-cleaning |  |  |  |
| - Thickness of walls & floor - Reinforcing details if not standard. |  |  |  |
| - Type of Grate (galvinised & to BCC standard) |  |  |  |
| - Lintel sizes (satisfactory for location & street flows) |  |  |  |
| - Gully to Gully connections only limited to 600mm dia. |  |  |  |
| - Surcharge structures details (UNDESIRABLE) |  |  |  |
| - Outlet geometry & location does not adversely impact on the downstream creek or adjoining properties. |  |  |  |
| - NO drowned outlets. |  |  |  |
| Pipe Outlet (Scour) Control |  |  |  |
| - Provided in accordance to Stormwater Outlets in Parks & Waterways Guidelines Version 2/2003. |  |  |  |
| - <1.5m/s velocity; rip rap apron provided with length 3 times pipe diameter - <2m/2 velocity; flatten pipe or upsize last pipe section to reduce to approx. 1.5m/s - >2m/s velocity; provide plunge pool rock armoured dissipater with typical length of 10 times pipe/RCBC diameter. (provide reasoning for other) |  |  |  |
| - Minimum riprap size is d50 300mm |  |  |  |
| - Outlets directed downstream of flow or tail-in channel created. |  |  |  |
| - Outlets to be placed at least: - 300mm above any natural waterway/creek level - 150mm above any vegetated swale/channel |  |  |  |
| - No bare earth channels; even if vegetated drawings. Should show jute mesh being used. |  |  |  |
| Catchment Plan |  |  |  |
| - Tabulation of catchment areas, slope, runoff coefficient, design discharges, etc. |  |  |  |
| - Layout with gully catchments |  |  |  |
| - Full drainage catchment shown including external with contours extending beyond limits of the site. |  |  |  |
| - Existing and proposed contours. |  |  |  |
| - Key overall site plan to be included if more than one catchment plan is required for larger sites. |  |  |  |
| Calculation Sheet (Refer to IDPSP – Section 7.7.2) |  |  |  |
| - Calculations confirm to QUDM & BCC supplement - Commercial & industrial catchments DO NOT use standard inlet time in Rational Method Calculations; instead adopt Tc < 10min for roof runoff. - Calculations prepared on standard BCC spreadsheet. |  |  |  |
| Detention Basin |  |  |  |
| Design |  |  |  |
| - Storage volume conforms with approved hydraulic report (if conditioned) |  |  |  |
| - Detention basin does not use Rational Method Tc. Use hydrological model to determine critical time for catchment. |  |  |  |
| - Minor system design ensures major flow can enter basin even if blockages of inlets occur (Q50 minor system design may be required in roads/driveways) |  |  |  |
| - Batters are at least 30% of perimeter of basin with minimum grades of: - Landscape edges 1V:4H - Grassed batters 1V:4H to 1V:6H - 1V:6H or flatter where publically accessible. |  |  |  |
| - Basin embankment crest min 3m width |  |  |  |
| - Outlets screened & set away from inlet pit to not interfere with hydraulics. |  |  |  |
| - Floor of Basin graded @ 2% - Subsoil drainage provided if <2% (or bio-retention water quality basin) - Min diameter of 100mm for branch lines & 150mm for collector line). |  |  |  |
| - Fencing only on top of retaining walls |  |  |  |
| - Inlets limited to two in number and located close to outlet to minimise scour from basin. |  |  |  |
| - Flood depth indicator gauge & warning sign provided. |  |  |  |
| - Turfed or vegetated |  |  |  |
| - Spillway detailed with 300mm freeboard to embankment and located where embankment height is lowest - Minor Flows to discharge via pipe outlet, NOT spillway. |  |  |  |
| Locations |  |  |  |
| - NOT TO BE higher than proposed lots or adjacent existing lots |  |  |  |
| - NOT TO BE higher than surrounding roads or public use areas. |  |  |  |
| - Spillway located in area where close to existing levels to reduce scour |  |  |  |
| Pump Storage (MCU’s) |  |  |  |
| - In accordance with Section 7.6.6 Pumped stormwater drainage of Chapter 7; IDPSP |  |  |  |
| - Pump systems must discharge directly to a gully / maintenance hole or drainage line |  |  |  |
| - All systems must provide an overflow to a soakage trench located along the boundary of the lowest part of the site - Trench design as per Section 7.6.8 of Ch.7; IDPSP |  |  |  |